## Slide 1: PlugNHarvest simulation model
Ana Constantin
Documentation
Last modified on 13.05.2019

## Slide 2: Clone or Download
Go to this link
Check if „issue520_PnH“ is selected
Clone or download the repository

## Slide 3: Aixlib with PnH in Dymola
Internal gains
Heating, cooling, ventilation
Ambient
conditions
Room model
Parameter Block / Fast Input mask

## Slide 4: Parameter Block
General: have to be set
Advanced: have default values, can be re-set if desired
Hidden (only on the model level): pre-set, since these values are rarely dependent on the use case. Can be re-set if desired, but we recommend re-setting them only in the simulation model, so the changes are noticeable.

## Slide 5: Components of simulation model
Model name
  AixLib.PlugNHarvest.Examples.Test
Main model
  Room envelope + internal gains + energy system + control
Boundary conditions
  Weather
  Schedules internal gains: occupants, lights, electrical appliances
  Schedules HVAC: heating cooling ventilation
Parameters for the whole model
  With the exception of one parameter, the whole
  simulation can be configured over this list of parameters
  Exception: the surface orientation for the calculation of the solar radiation on the facade
    In the weather model: Surface orientation data (chose or create a record with the needed orientation)
    Connect the correct solar output from the weather model to the room model (if a record with 4 orientations is provided, and the third orientation is needed, connect the third element of the output vector )

## Slide 6: Parameters
General: have to be set theoretically foe each use case
Advanced: have default values, can be re-set if desired for each use
Hidden (only on the model level): pre-set, since these values are rarely dependent on the use case. Can be re-set if desired, but we recommend re-setting them only in the simulation model, so the changes are noticeable.
  Might be that the list in the presentation is incomplete, since this exceeds goal of the presentation
Parameters for the whole model
  Air model (moist air)

## Slide 7: Type of room - Envelope
One outer wall, the rest inner walls towards the building
Parameters:
  General:
    room height, length and width
    wall types
    window type
  Advanced
    Outer walls: solar absorbance, heat convection model
    Sunblind
    Infiltration
    Heat bridge
  Hidden
    Initial temperatures of walls

## Slide 8: Type of room - Smart facade
General
  Choosing the elements of the facade
  Parameters for PV: number of panels, record, maximal power output
  Parameters for solar heater
Advanced
Hidden

## Slide 9: Internal gains
Persons
  General:
    density of occupants
    heat output from activity
  Advanced
    ratio convective heat from total heat output
  Hidden
    Start temperature, surface area for a human, temperature dependence of heat output
Lights & electrical appliances
  General
    Specific Pel/m2 for light source / appliances
  Advanced
    Coefficient Pth/Pel for lights / appliances
    Coefficient Pth,radiative/Pel for lights / appliances
  Hidden
    Emissivity of lights / appliances

## Slide 10: Energy system + Control
Parameters
  General
    Maximal power output for heater / cooler
    Set temperature for heating / cooling
    Outside temperature under which heater starts
  Advanced
    Is heater / cooler electric
    Electrical efficiency of heater / cooler
  Hidden
    Parameters for internal PI controllers

## Slide 11: Boundary conditions
Parameters
  General
    Latitude and longitude of location
    File for weather data
    Schedules for internal gains and HVAC
  Advanced
  Hidden
    Ground reflection for weather model
    Model used for solar radiation
    Output from weather model
    Interpolation of data from tables
    Extrapolation of data from tables: periodic

## Slide 12: Some examples for setting parameters for an office
Sources for the values are given and detailed at the end of the presentation in the Bibliography
Internal gains
  Persons
    Density
    Schedule – in the simulation model a simpler profile 09:00 – 17:00 is used
  Lights & electrical appliances
    Modelling
    Types
    Schedule - in the simulation model a simpler profile 09:00 – 17:00 is used
Energy system
  Efficiency for different types of equipment
  Control: set temperatures

## Slide 13: Internal gains – Persons - User density
Zone | Density | Source
Office | 0.06 / 0.07 / 0.1 Persons / m2 | DIN 18599-10.2 (A.2), GER
 | 0.4 Persons / m2 | ASHRAE 90.1 – Table G-B, US

## Slide 14: Internal gains – Persons – Presence profiles (ASHRAE 90.1_G)
Service / Office

## Slide 15: Internal gains – Persons – Monthly variation (Source SIA 2024)
Office (2-6 Persons)

## Slide 16: Internal gains – Lighting and electrical appliances
Equipment such as lighting and auxiliary machines (computers, ovens, cooling boxes) depends on zone type and leads to an electrical and thermal load
Data needed for modelling lighting and auxiliary machines
  Load profiles (percentual) depending on zone type  table
  Electrical or heat load equipment based on zone type / type of activity  constant, one value in W/m²
  Efficiency electrical to thermal for type of equipment  constant, one value
Parameters:
Zone Area
Specific Pelectric / m2 for zone type
Coefficient Pthermal from Pelectric
Coefficient Pth,rad from Pthermal
Emissivity
Schedule
Pth,conv
Pth,rad
Pel

## Slide 17: Internal Gains – Lights - Requirements
Zone | Heat load | Energy requirement | Source
Office | 500 lx 0.8 m | 25 Wel/m2 – Halogen 9 Wel/m2 – Flourescent 5 Wel/m2 – LED | DIN 18599-10.2 (A2) CommONEnergy2013 (Fig 38, Page 64)
 | 12 Wth/m2 | 13 Wel/m2 90% @[WWW1] | Clark2015, Table A2, US
 |  | 47 / 41 / 22 / 13 / 8 Wel/m2 | VDI 3807-4, Table 3, (2) GER

## Slide 18: Internal gains – Lights - Type of lamps
Source: CommONEnergy
Source: CIBSE, Guide A

## Slide 19: Internal gains – Lights - Efficiency
Source [WWW1]
Source: CIBSE, Guide A

## Slide 20: Internal gains – Lights - Profiles (ASHRAE 90.1_G)
Service / Office

## Slide 21: Internal gains – Appliances
Auxiliary machines (based on [ASHRAE_Fundamentals_2001])
  Office – used for office
      Heat gain 50% of rated hourly input  100 % sensible (22% radiant, 78 % convective as a mean between equipment with fans and without fans)
Zone | Heat load | Schedule | Source
Office | 2.8 / 7.1 / 15 W/m2 (small, middle, high) | 6 full h / d | DIN 18599-10.2 (A2)

## Slide 22: Energy system – Temperature and Ventilation, requirements
Zone | Heating / Cooling / Ventilation with outside air
Office (2-6 persons) | 21 °C / 24 °C / 4 m3/(h*m2) DIN 18599-10.2 (A2)

## Slide 23: Energy System - Efficiency
Type of equipment | Efficiency (available for different years)
Boiler - Gas | Seasonal efficiency 86-95% 102-108% (condensation boiler) Source: [Worm2015]
Heat pump | COP (coefficient of performance): 1.9-4.3 DIN 18599-5, Annex C
Chiller | EER (energy efficiency ratio): 2.9 -5.9 (DIN 18599-7, Table 25)
Air conditioning | EER: 2.6 – 3.4 Heat recovery efficiency: 50% Specific fan power (kW/(m3/s)): 1.5 Source: [Worm2015], DIN 18599-7, Table 6, 29

## Slide 24: Bibliography
[ASHRAE 90.2] - ASHRAE 90.1 - User Manual Appendix G: Building Performance Rating Method, 2004.
[ASHRAE_Fundamentals_2001] - 2001 ASHRAE Fundamentals Handbook (SI), Appliances
[CIBSE, Guide A] - Environmental design, 2006
[Clark2015] – Clark, J. , Energy-Efficient Supermarket Heating, Ventilation, and Air Conditioning in Humid Climates in the United States, Technical Report, NREL/TP-5500-63796, National Renewable Energy Laboratory, Denver, CO, USA March 2015
[CommONEnergy] - CommONEnergy: Re-conceptualize shopping malls from consumerism to energy conservation, D2.2, Deliverable 2.2: Shopping malls inefficiencies, 2015
[DIN 18599] Calculation of the net, final and primary energy demand for heating, cooling, ventilation, domestic hot water and lighting
  Part 7: Final energy demand of air-handling and air-conditioning systems for non-residential buildings
  Part 10: Boundary conditions of use, climatic data

## Slide 25
[SIA2024] - SIA Merkblatt 2024 Standard-Nutzungsbedingungen für die Energie- und Gebäudetechnik, 2006
[VDI3807-4] - Characteristic values of energy and water consumption of buildings Characteristic values for electrical energy, 2008
[Worm2015] – Worm; Rathert, Bekanntmachung der Regeln zur Datenaufnahme und Datenverwendung im Nichtwohngebäudebestand. Bundesministeriums für Wirtschaft und Energie und des Bundesministeriums für Umwelt, Naturschutz, Bau und Reaktorsicherheit, Berlin, Germany, 7.03.2015
[WWW1] - http://bigladdersoftware.com/epx/docs/8-0/engineering-reference/page-089.html  Heat gains from lights